## Main
CAN ID
| 20---28 | 19 | 11---18 | 3---10 | 2 | 1 | 0
| PROTNO | PTP | destination address | source address | CNT | reserved(1) | reserved(1)
PTP 0:broadcast mode; 1:address mode
CNT 1:more frame datas;
PROTNO 0x060 :communications between rectifiers and controller;
between rectifiers,if destination address is 0xff,thus this is broadcast frame for rectifiers
source address is rectifier's actual address
frame format
ERR | MSGTYPE | ErrType | ValueType |  | Value
1bit（0） | 7bits | 1byte | 2bytes |  | 4bytes
Byte0 |  | Byte1 | Byte2 | Byte3 | Byte4 | Byte5 | Byte6 | Byte7
MDL_H |  |  | MDL_L |  | MDH_H |  | MDH_L
ErrType:0xF0 normal frame; OxF1 address err; 0xF2 communication fail;
,0x41:inqui
MSGTYPE:in the condition of rectifier response,0x41:data inquiry response;0x42:data configuration response
MSGTYPE:for controller,0x01:inquiry command; 0x02:data configuration command
ValueType |  |  |  |  | ValueType |  |  |  | ValueType
0x03 | inquiry for rectifier's output voltage |  |  |  | 0x01 | set rectifier's output voltage（not save） |  |  | 0x10 | on/off control（Value=1on）
0x04 | inquiry for rectifier's output current |  |  |  | 0x02 | set rectifier's limiting current point |  |  | 0x11 | fan speed control(1=full speed 0=auto)
0x03 | inquiry for rectifier's sink temperature |  |  |  | 0x03 | set rectifier's default float charging voltage
0x05 | inquiry for rectifier's AC input voltage |  |  |  | 0x04 | set rectifier's overvoltage protection high limit of output voltage
0x06 | inquiry for rectifier's PFC voltage |  |  |  | 0x05 | set rectifier's overtemperature protection high limit
0x07 | temperature1 |  |  |  | 0x0e | set rectifier's id
0x08 | temperature2 |  |  |  | 0x0F | clear total runing time of rectifier
0x09 | rotation speed of fan
0x0B | err info(see table1)
0x0D | state info(see table1)
0x0E | secondary soft version
0x0F | primary soft version
0x26 | rectifier's id
0x27 | total running time for rectifier(hour)
0x2A | default float charging voltage
0x2B | default limiting current point
Floating point number sending order:floating point number format consists of four bytes,send data bits by HEX-ASCII format.sending four byte is such as:sign&exponent(1 byte),mantissa high bits(1 byte),mantissa middle bits(1 byte),mantissa low bits(1 byte).IEEE32 bits float point number format(standard c language float point number format) is used in the protocol,format is such as:
D31 | D30—D23 | D22—D16 | D15—D8 | D7—D0
sign | exponent | mantissa high bits | mantissa middle bits | mantissa low bits
if exponent=E，mantissa is M，the value of float point number=±（1+M×2-23）·2E-127
for example:when float point number is 40H，A0H，00H，00H，that is to say S=0，E=129，M=221，and thus float point number =（1+221×2-23）·2129-127=5.0。If float point number= 60，according four bytes by ascii code is such as：0x42，0x70，0x00，0x00，sending order is 0x42，0x70，0x00，0x00。If float point number=1.2，according four bytes by ascii code is such as：0x3f，0x99，0x99，0x9a，sending order is 0x3f，0x99，0x99，0x9a 。
for example:
data inquiry ID=0x6080003
output voltage inquiry command data :03 f0 00 01 00 00 00 00
table 1
err&alarm info |  |  | state info
errcode | err info |  | statecode | state info
0001H | Dc output overvoltage |  | 0001H | on/off state(0on 1off)
0002H | Dc output undervoltage |  | 0002H | fan control atate(1full 0auto)
0004H | Dc output overcurrent |  | 0004H | minor current sharing err
0008H | CAN ID abnormal |  | 0008H | primary current sharing err
0010H | secondary 232comm abnormal |  | 0010H | 1:relay close
0020H | primary 232comm abnormal |  | 0020H | 1:PFC enable
0040H | AC overvoltage |  | 0040H | 1:LLC enable
0080H | AC undervoltage
0100H | PFC overvoltage
0200H | PFC undervoltage
0400H | sink overtemperature
0800H | environment overtemperature
1000H | fan err